## 电价
Time | Electricity Price (元/kWh) | Electricity Price ($/kWh) |  | 5:30-7:00 | 0.5608 | 0-5:30 | 0.2928 | 每隔半小时 | 1 | 0.2928
5:30-7:00 | 0.5608 | 0.087625 |  | 7:00-8:00 | 0.80199 | 5:30-7:00 | 0.5608 |  | 2 | 0.2928
7:00-8:00 | 0.80199 | 0.12531 |  | 8:00-9:00 | 0.5608 | 7:00-8:00 | 0.80199 |  | 3 | 0.2928
8:00-9:00 | 0.5608 | 0.087625 |  | 9:00-11:30 | 0.80199 | 8:00-9:00 | 0.5608 |  | 4 | 0.2928
9:00-11:30 | 0.80199 | 0.12531 |  | 11:30-12:00 | 0.5608 | 9:00-11:30 | 0.80199 |  | 5 | 0.2928
11:30-12:00 | 0.5608 | 0.087625 |  | 12:00-14:00 | 0.2928 | 11:30-12:00 | 0.5608 |  | 6 | 0.2928
12:00-14:00 | 0.2928 | 0.04575 |  | 14:00-15:30 | 0.5608 | 12:00-14:00 | 0.2928 |  | 7 | 0.2928
14:00-15:30 | 0.5608 | 0.087625 |  | 15:30-20:00 | 0.80199 | 14:00-15:30 | 0.5608 |  | 8 | 0.2928
15:30-20:00 | 0.80199 | 0.12531 |  | 20:00-23:30 | 0.5608 | 15:30-20:00 | 0.80199 |  | 9 | 0.2928
20:00-23:30 | 0.5608 | 0.087625 |  | 23:30-5:30 | 0.2928 | 20:00-23:30 | 0.5608 |  | 10 | 0.2928
23:30-5:30 | 0.2928 | 0.04575 |  |  |  | 23:30-24:00 | 0.2928 |  | 11 | 0.2928
黑龙江峰谷时段的划分参考：https://drc.hlj.gov.cn/drc/c111446/202410/c00_31776227.shtml | [8 empty] | 12 | 0.5608
[9 empty] | 13 | 0.5608
[9 empty] | 14 | 0.5608
[9 empty] | 15 | 0.80199
[9 empty] | 16 | 0.80199
[9 empty] | 17 | 0.5608
https://www.drbt.gov.cn/duerbote/yzdrbtp/202308/309547/files/2%E3%80%81%E5%9B%BD%E7%BD%91%E9%BB%91%E9%BE%99%E6%B1%9F%E7%9C%81%E7%94%B5%E5%8A%9B%E6%9C%89%E9%99%90%E5%85%AC%E5%8F%B8%E5%B7%A5%E5%95%86%E4%B8%9A%E4%BB%A3%E7%90%86%E8%B4%AD%E7%94%B5%E7%94%B5%E4%BB%B7%E8%A1%A8.pdf |  |  | https://ele.aiit.org.cn/static/elefile/99308281706007471872401734071331.pdf | [5 empty] | 18 | 0.5608
[9 empty] | 19 | 0.80199
[9 empty] | 20 | 0.80199
[9 empty] | 21 | 0.80199
[9 empty] | 22 | 0.80199
[9 empty] | 23 | 0.80199
[9 empty] | 24 | 0.5608
[9 empty] | 25 | 0.2928
[9 empty] | 26 | 0.2928
[9 empty] | 27 | 0.2928
[9 empty] | 28 | 0.2928
[9 empty] | 29 | 0.5608
[9 empty] | 30 | 0.5608
[9 empty] | 31 | 0.5608
[9 empty] | 32 | 0.80199
[9 empty] | 33 | 0.80199
[9 empty] | 34 | 0.80199
[9 empty] | 35 | 0.80199
[9 empty] | 36 | 0.80199
[9 empty] | 37 | 0.80199
[9 empty] | 38 | 0.80199
[9 empty] | 39 | 0.80199
[9 empty] | 40 | 0.80199
[9 empty] | 41 | 0.5608
[9 empty] | 42 | 0.5608
[9 empty] | 43 | 0.5608
[9 empty] | 44 | 0.5608
[9 empty] | 45 | 0.5608
[9 empty] | 46 | 0.5608
[9 empty] | 47 | 0.5608
[9 empty] | 48 | 0.2928

## 经济参数
Technology | priceinv | priceOM,fid | priceOM,var | 折旧年限 | Technology | priceinv | priceOM,fid | priceOM,var | Technology | priceinv | priceOM,fid | priceOM,var
| (106RMB/MW)相当于元/W | (103RMB/MW/year) | (RMB/(MW·h)) | year |  | ($/MW) | ($/MW/year) | ($/(MW·h)) |  | (105$/MW) | (103$/MW/year) | ($/(MW·h))
GT | 2.97 | 36.8 | 14.49 | 30 | GT | 412500 | 5111.1111 | 2.0125 | GT | 4.125 | 5.1111 | 2.0125
PV | 4.8312 | 27.36 | 0 | 20 | PV | 671000 | 3800 | 0 | PV | 6.71 | 3.8 | 0
WT | 7.0992 | 165.6615 | 0 | 20 | WT | 986000 | 23008.5373 | 0 | WT | 9.86 | 23.0085 | 0
EB电锅炉 | 1.1 | 13.76 | 0 | 20 | EB | 152777.7778 | 1911.1111 | 0 | EB | 1.5278 | 1.9111 | 0
NGB燃气锅炉 | 1.5 | 10 | 12 | 20 | NGB | 208333.3333 | 1388.8889 | 1.875 | NGB | 2.0833 | 1.3889 | 1.875
EHP电热泵 | 3.8 | 17.66 | 0 | 20 | EHP | 527777.7778 | 2452.7778 | 0 | EHP | 5.2778 | 2.4528 | 0
GAHP燃气吸收式热泵 | 4.5 | 20 | 15 | 20 | GAHP | 625000 | 2777.7778 | 2.3438 | GAHP | 6.25 | 2.7778 | 2.3438
BESS | 5.4432 | 230.4 | 0 | 15 | BESS | 756000 | 32000 | 0 | BESS | 7.56 | 32 | 0
TESS | 0.36 | 0.12 | 0 | 20 | TESS | 50000 | 16.6667 | 0 | TESS | 0.5 | 0.016667 | 0
| 90元/kWh | 360元/kW |  |  |  | 189*4*1000=756000 | 8*4*1000=32000
燃机成本来源：【2024】Enhancing accuracy of flexibility characterization in integrated energy system design: A variable temporal resolution optimization method
https://www.sciencedirect.com/science/article/pii/S0360544223031985
| IRENA_Renewable_power_generation_costs_in_2023 |  |  | 运维成本和2021年基本持平 | 美国41$/kW/yr，1757：986=41：O&M of China |  |  | https://www.nrel.gov/docs/fy25osti/91775.pdf
可再生成本下降率：
【2050下降50%左右，差不多每年3%，World Energy Outlook 2017, International Energy Agency】
储电成本：An evaluation of energy storage cost and performance characteristics
https://www.mdpi.com/1996-1073/13/13/3307
By 2030, the installed costs of battery storage systems could fall by 50-66%
年下降率：15%
https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2017/Oct/IRENA_Electricity_Storage_Costs_2017.pdf
电热泵、电锅炉、储热成本：Planning multiple energy systems for low-carbon districts with high penetration of renewable energy: An empirical study in China
https://www.sciencedirect.com/science/article/pii/S030626191932077X

## 技术参数
GT | 48 | 20% | 0.569 | 0.05 | 5 | 实际数据
PV | - | 10% | - | - | 1
WT | - | 10% | - | - | 1
EB | 5 | 20% | 0.9 | 0.05 | 1
NGB | 10 | 30% | 0.8 | 0.05 | 10 | 实际数据：70-85%
EHP | 10 | 10% | 3 | 0.1 | 1
GAHP | 4 | 15% | 1.3 | 0.1 | 5 | https://www.rehva.eu/rehva-journal/chapter/gas-driven-absorption-heat-pumps-in-domestic-heating
BESS | - | 0% | 0.92 | - | 1
TESS | - | 0% | 0.95 | - | 15
燃机技术参数来源：qinyuxiao变时间分辨率文献：Enhancing accuracy of flexibility characterization in integrated energy system design: A variable temporal resolution optimization method
电热泵、电锅炉、储热成本：Planning multiple energy systems for low-carbon districts with high penetration of renewable energy: An empirical study in China

## 装机情况
Technology |  | GT | PV | WT | 电锅炉EB | 燃气锅炉NGB | 电热泵EHP | 燃气热泵GAHP | BES1 功率 | BES2 容量 | TES1 蒸汽 | TES2 热水
The optimal capacity（MW） | Case1 | 96 | 0 | 0 | 0 | 360 | 0 | 12 | 0 | 0 | 0 | 0
| Case2（100MW） | 192 | 0 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874
| Case3（0MW） | 240 | 55.7914 | 74.0249 | 0 | 90 | 0 | 276 | 2.3659 | 0 | 0 | 53.0874 |  |  | 240 | 55.7914 | 74.0249 | 0 | 90 | 0 | 276 | 2.3659 | 53.0874
| Case4 | 288 | 1.6424 | 0 | 15 | 60 | 290 | 24 | 0 | 0 | 0 | 157.797 |  |  | 192 | 44.7161 | 56.1849 | 0 | 90 | 0 | 276 | 1.9604 | 53.0874
| a_result_cap | [13 empty] | 192 | 34.6681 | 39.9624 | 0 | 90 | 0 | 276 | 1.676 | 53.0874
[15 empty] | 192 | 28.3539 | 29.9582 | 0 | 90 | 0 | 276 | 1.421 | 53.0874
case2-3 | 购电上限： | [13 empty] | 192 | 22.4832 | 23.0177 | 0 | 90 | 0 | 276 | 1.0642 | 53.0874
| 2MW | 192 | 44.7161 | 56.1849 | 0 | 90 | 0 | 276 | 1.9604 | 0 | 0 | 53.0874 |  |  | 192 | 17.3001 | 15.8035 | 0 | 90 | 0 | 276 | 0.77452 | 53.0874
| 4MW | 192 | 34.6681 | 39.9624 | 0 | 90 | 0 | 276 | 1.676 | 0 | 0 | 53.0874 |  |  | 192 | 13.7128 | 7.9539 | 0 | 90 | 0 | 276 | 0.4888 | 53.0874
| 6MW | 192 | 28.3539 | 29.9582 | 0 | 90 | 0 | 276 | 1.421 | 0 | 0 | 53.0874 |  |  | 192 | 11.4065 | 0 | 0 | 90 | 0 | 276 | 0.29539 | 53.0874
| 8MW | 192 | 22.4832 | 23.0177 | 0 | 90 | 0 | 276 | 1.0642 | 0 | 0 | 53.0874 |  |  | 192 | 7.6147 | 0 | 0 | 90 | 0 | 276 | 0 | 53.0874
| 10MW | 192 | 17.3001 | 15.8035 | 0 | 90 | 0 | 276 | 0.77452 | 0 | 0 | 53.0874 |  |  | 192 | 0.20392 | 0 | 0 | 90 | 0 | 276 | 0 | 53.0874
| 12MW | 192 | 13.7128 | 7.9539 | 0 | 90 | 0 | 276 | 0.4888 | 0 | 0 | 53.0874 |  |  | 192 | 0 | 0 | 0 | 90 | 0 | 276 | 0 | 53.0874
| 14MW | 192 | 11.4065 | 0 | 0 | 90 | 0 | 276 | 0.29539 | 0 | 0 | 53.0874 |  |  | 192 | 0 | 0 | 0 | 90 | 0 | 276 | 0 | 53.0874
| 16MW | 192 | 7.6147 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  |  | 192 | 0 | 0 | 0 | 90 | 0 | 276 | 0 | 53.0874
| 18MW | 192 | 0.20392 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874
| 20MW | 192 | 0 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 | 购电上限20MW的时候，已经没有可再生能源了，此时主要是依赖电网和燃机，如果电价和碳价上涨，会出现需要可再生能源的临界点
| 30MW | 192 | 0 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874
case1不变
case2 100MW购电上限 |  | GT | PV | WT | EB | NGB | EHP | GAHP | BES1 功率 | BES2 容量 | TES1 蒸汽 | TES2 热水
| 碳价100 | 192 | 0 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  | 0
| 200 | 192 | 5.9646 | 0 | 0 | 20 | 0 | 344 | 0 | 0 | 0 | 61.0874 |  | 5.9646
| 300 | 192 | 19.2394 | 0 | 0 | 10 | 0 | 356 | 0 | 0 | 0 | 53.0874 |  | 19.2394
| 400 | 192 | 82.7647 | 0 | 0 | 10 | 0 | 356 | 0 | 0 | 0 | 53.0874 |  | 82.7647
| 500 | 192 | 164.2932 | 177.5599 | 0 | 10 | 0 | 356 | 0 | 0 | 0 | 53.0874 |  | 341.853
| 600 | 192 | 204.476 | 206.5741 | 0 | 10 | 0 | 356 | 0 | 0 | 0 | 53.0874 |  | 411.0502
| 700 | 192 | 213.2805 | 219.0336 | 0 | 10 | 0 | 360 | 0 | 0 | 0 | 37.0874 |  | 432.3141
| 800 | 192 | 225.7076 | 241.7298 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 61.0874 |  | 467.4373
| 900 | 192 | 251.5095 | 260.1908 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 61.0874 |  | 511.7003
| 1000 | 192 | 267.0339 | 267.8531 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 61.0874 |  | 534.887
0
case3 0MW购电上限 |  | GT | PV | WT | EB | NGB | EHP | GAHP | BES1 功率 | BES2 容量 | TES1 蒸汽 | TES2 热水 |  | #VALUE!
| 碳价100 | 240 | 55.7914 | 74.0249 | 0 | 90 | 0 | 276 | 2.3659 | 0 | 0 | 53.0874 |  | 129.8162
| 200 | 240 | 57.6278 | 92.5994 | 0 | 20 | 0 | 344 | 2.4421 | 0 | 0 | 61.0874 |  | 150.2272
| 300 | 240 | 59.5522 | 121.1124 | 0 | 10 | 0 | 356 | 2.4988 | 0 | 0 | 53.0874 |  | 180.6646
| 400 | 240 | 88.7715 | 145.7256 | 0 | 10 | 0 | 356 | 2.4959 | 0 | 0 | 53.0874 |  | 234.4971
| 500 | 240 | 148.5518 | 177.6982 | 0 | 10 | 0 | 356 | 2.5053 | 0 | 0 | 53.0874 |  | 326.2501
| 600 | 240 | 182.0816 | 206.5741 | 0 | 10 | 0 | 356 | 2.5053 | 0 | 0 | 53.0874 |  | 388.6557
| 700 | 240 | 201.1687 | 232.3957 | 0 | 10 | 0 | 356 | 2.5053 | 0 | 0 | 53.0874 |  | 433.5644
| 800 | 240 | 204.517 | 244.0348 | 0 | 0 | 0 | 364 | 2.5053 | 0 | 0 | 61.0874 |  | 448.5518
| 900 | 240 | 217.8954 | 260.2338 | 0 | 0 | 0 | 364 | 2.5053 | 0 | 0 | 61.0874 |  | 478.1291
| 1000 | 240 | 251.5128 | 260.2338 | 0 | 0 | 0 | 364 | 2.5053 | 0 | 0 | 61.0874 |  | 511.7465
0
| case4 | GT | PV | WT | EB | NGB | EHP | GAHP | BES1 功率 | BES2 容量 | TES1 蒸汽 | TES2 热水 |  | #VALUE!
| 碳价100 | 288 | 1.6424 | 0 | 15 | 60 | 290 | 24 | 0 | 0 | 0 | 157.797 |  | 1.6424
| 200 | 336 | 5.2284 | 0 | 45 | 0 | 360 | 0 | 0 | 0 | 0 | 39.3961 |  | 5.2284
| 300 | 336 | 5.4243 | 0 | 45 | 0 | 360 | 0 | 0 | 0 | 0 | 39.0153 |  | 5.4243
| 400 | 336 | 83.651 | 0 | 45 | 0 | 360 | 0 | 0 | 0 | 0 | 29.2018 |  | 83.651
| 500 | 336 | 193.8873 | 301.713 | 45 | 0 | 360 | 0 | 0 | 0 | 0 | 30.3695 |  | 495.6003
| 600 | 336 | 314.6447 | 369.7211 | 75 | 0 | 360 | 0 | 0 | 0 | 0 | 128.9878 |  | 684.3658
| 700 | 336 | 401.1062 | 430.5737 | 125 | 0 | 360 | 0 | 0 | 0 | 0 | 301.7912 |  | 831.68
| 800 | 336 | 466.0018 | 492.8586 | 180 | 0 | 360 | 0 | 0 | 0 | 0 | 360.7325 |  | 958.8604
| 900 | 288 | 555.8539 | 682.4759 | 285 | 0 | 350 | 0 | 0 | 0 | 0 | 1068.086 |  | 1238.3298
| 1000 | 288 | 642.0968 | 725.6982 | 340 | 0 | 340 | 0 | 0 | 0 | 29.4342 | 1325.8034 |  | 1367.7949
case1装机不变
| case2 | GT | PV | WT | EB | NGB | EHP | GAHP | BES1 功率 | BES2 容量 | TES1 蒸汽 | TES2 热水
| 1倍 | 192 | 0 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874
| 1.1 |  | 0 | [10 empty] | 1 | 0
| 1.2 |  | 0 | [10 empty] | 1.1 | 0
| 1.3 |  | 0 | [10 empty] | 1.2 | 0
| 1.4 |  | 0 | [10 empty] | 1.3 | 0
| 1.5 |  | 0.089669 | [10 empty] | 1.4 | 0
| 1.6 |  | 1.3663 | [10 empty] | 1.5 | 0.089669
| 1.7 |  | 2.2894 | [10 empty] | 1.6 | 1.3663
| 1.8 |  | 2.9116 | [10 empty] | 1.7 | 2.2894
| 1.9 |  | 3.3764 | [10 empty] | 1.8 | 2.9116
| 2倍 | 192 | 3.9442 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  | 1.9 | 3.3764
| 3倍 | 192 | 9.3663 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  | 2 | 3.9442
| 4倍 | 192 | 16.3819 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  | 3 | 9.3663
| 5倍 | 192 | 21.8567 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  | 4 | 16.3819
| 6倍 | 192 | 22.7594 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  | 5 | 21.8567
| 7倍 | 192 | 25.4902 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  | 6 | 22.7594
| 8倍 | 192 | 27.1244 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  | 7 | 25.4902
| 9倍 | 192 | 30.0891 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  | 8 | 27.1244
| 10倍 | 192 | 31.6832 | 0 | 0 | 90 | 0 | 276 | 0 | 0 | 0 | 53.0874 |  | 9 | 30.0891
[14 empty] | 10 | 31.6832
case3装机不变
case4装机不变
[25 empty] | 240 | 168.9508 | 206.5741 | 0 | 360 | 0 | 360 | 2.1255 | 7.329
[25 empty] | 192 | 178.0736 | 205.6716 | 0 | 360 | 0 | 360 | 0.70824 | 6.6675
[25 empty] | 192 | 209.6099 | 206.5741 | 0 | 360 | 0 | 360 | 0 | 7.0041
[25 empty] | 192 | 200.2342 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 7.0041
[25 empty] | 192 | 200.2342 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 8.2064
[16 empty] | 240 | 168.9508 | 206.5741 | 0 | 360 | 0 | 360 | 0 | 7.329 | 192 | 202.8269 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 9.3949
[16 empty] | 192 | 178.0736 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 6.6675 | 192 | 200.2342 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 7.0041
[16 empty] | 192 | 209.6099 | 206.5741 | 0 | 360 | 0 | 360 | 0 | 7.0041 | 192 | 204.8218 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 6.468
[16 empty] | 192 | 200.2342 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 7.0041 | 192 | 204.8844 | 205.5082 | 0 | 360 | 0 | 360 | 0 | 7.2306
[16 empty] | 192 | 200.2342 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 8.2064 | 192 | 204.8218 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 7.2306
[16 empty] | 192 | 202.8269 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 9.3949 | 192 | 204.8218 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 6.6675
[16 empty] | 192 | 200.2342 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 7.0041
[16 empty] | 192 | 204.8218 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 6.468
[16 empty] | 192 | 204.8844 | 205.5082 | 0 | 360 | 0 | 360 | 0 | 7.2306
[16 empty] | 192 | 204.8218 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 7.2306
[16 empty] | 192 | 204.8218 | 205.6716 | 0 | 360 | 0 | 360 | 0 | 6.6675

## 成本
| 总成本l/($/year) | 投资成本/ ($/year) | 运维成本/ ($/year) | 燃料成本/ ($/year) | 购电成本/ ($/year) | 碳排放成本/ ($/year) |  |  | 总成本 | 投资成本 | 运维成本 | 燃料成本 | 购电成本 | 碳排放成本
Case1 | 505412215.675 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 35795120.1637 | [8 empty] | 505.4122 | 13.2826 | 2.2483 | 408.1819 | 45.9044 | 35.7951
Case2(无购电上限) | 157887796.8408 | 29600974.4591 | 8661026.8512 | 103956831.5206 | 507319.2557 | 15161598.7542 | 0.68761 | 0.68761
Case3(0MW) | 172517414.6641 | 44667871.5627 | 16026218.1688 | 97859427.8171 | 0 | 13209186.4258 | 9.266% | 0.65866 | 9.266% | 50.9% | 85.04% | -5.865% | -100% | -12.88%
Case4 | 143666198.9661 | 33394565.1297 | 7021808.777 | 95272212.8998 | 0 | 7975179.3133 | 16.72% | 0.71574 | -16.72% | -25.24% | -56.19% | -2.644% | #DIV/0! | -39.62%
| a_result_cost | 505.4122 | 81.74%
143663766.1198
购电上限： | [7 empty] | 购电上限： | 总成本l/(10^6$/year) | 投资成本/ (10^6$/year) | 运维成本/ (10^6$/year) | 燃料成本/ (10^6$/year) | 购电成本/ (10^6$/year) | 碳排放成本/ (10^6$/year)
0MW | 172517414.6641 | 44667871.5627 | 16026218.1688 | 97859427.8171 | 0 | 13209186.4258 |  | 0MW | 172.5174 | 44.6679 | 16.0262 | 97.8594 | 0 | 13.2092
2MW | 167809286.7879 | 39755030.4405 | 14577383.8636 | 99262894.2341 | 52187.2018 | 13608861.9091 |  | 2MW | 167.8093 | 39.755 | 14.5774 | 99.2629 | 0.052187 | 13.6089
4MW | 165476230.814 | 37127035.8545 | 13329927.2321 | 100544498.9124 | 106533.1077 | 13977909.7483 |  | 4MW | 165.4762 | 37.127 | 13.3299 | 100.5445 | 0.10653 | 13.9779
6MW | 163467674.9101 | 35472283.2973 | 12035310.4118 | 101311914.9726 | 165577.3206 | 14220526.9126 |  | 6MW | 163.4677 | 35.4723 | 12.0353 | 101.3119 | 0.16558 | 14.2205
8MW | 161808677.5887 | 34155570.4814 | 10947460.9336 | 101887863.6669 | 228632.39 | 14420512.7065 |  | 8MW | 161.8087 | 34.1556 | 10.9475 | 101.8879 | 0.22863 | 14.4205
10MW | 160525504.3369 | 32881563.9985 | 10173946.5008 | 102483426.3288 | 269469.8942 | 14605367.8634 |  | 10MW | 160.5255 | 32.8816 | 10.1739 | 102.4834 | 0.26947 | 14.6054
12MW | 159463027.0477 | 31658397.848 | 9566579.3935 | 103058055.3671 | 317150.3234 | 14789142.7707 |  | 12MW | 159.463 | 31.6584 | 9.5666 | 103.0581 | 0.31715 | 14.7891
14MW | 158558423.4078 | 30548976.7042 | 9036564.3607 | 103587358.7778 | 374834.144 | 14966359.6664 |  | 14MW | 158.5584 | 30.549 | 9.0366 | 103.5874 | 0.37483 | 14.9664
16MW | 158034577.4688 | 30171238.4958 | 8677216.506 | 103716482.2408 | 413028.9951 | 15025214.7621 |  | 16MW | 158.0346 | 30.1712 | 8.6772 | 103.7165 | 0.41303 | 15.0252
18MW | 157893779.578 | 29616246.1943 | 8661028.6443 | 103948197.4769 | 506810.6512 | 15160501.0047 |  | 18MW | 157.8938 | 29.6162 | 8.661 | 103.9482 | 0.50681 | 15.1605
20MW | 157886407.262 | 29600974.4591 | 8661442.6721 | 103957173.3213 | 505556.7584 | 15161212.0512 |  | 20MW | 157.8864 | 29.601 | 8.6614 | 103.9572 | 0.50556 | 15.1612
22MW | 157887796.8408 | 29600974.4591 | 8661026.8512 | 103956831.5206 | 507319.2557 | 15161598.7542 |  | 22MW | 157.8878 | 29.601 | 8.661 | 103.9568 | 0.50732 | 15.1616
24MW | 157887796.8408 | 29600974.4591 | 8661026.8512 | 103956831.5206 | 507319.2557 | 15161598.7542 | 9.266% | 24MW | 157.8878 | 29.601 | 8.661 | 103.9568 | 0.50732 | 15.1616
case1 | 总成本l/($/year) | 投资成本/ ($/year) | 运维成本/ ($/year) | 燃料成本/ ($/year) | 购电成本/ ($/year) | 碳排放成本/ ($/year)
碳价100 | 505412215.675 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 35795120.1637 | 63.74% | 505.4122 | 35.7951
200 | 541207335.8387 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 71590240.3273 | 322.1561 | 541.2073 | 71.5902
300 | 577002456.0024 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 107385360.491 |  | 577.0025 | 107.3854
400 | 612797576.166 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 143180480.6546 |  | 612.7976 | 143.1805
500 | 648592696.3297 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 178975600.8183 |  | 648.5927 | 178.9756
600 | 684387816.4933 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 214770720.9819 |  | 684.3878 | 214.7707
700 | 720182936.657 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 250565841.1456 |  | 720.1829 | 250.5658
800 | 755978056.8206 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 286360961.3093 |  | 755.9781 | 286.361
900 | 791773176.9843 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 322156081.4729 |  | 791.7732 | 322.1561
1000 | 827568297.148 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 357951201.6366 |  | 827.5683 | 357.9512
[8 empty] | 0 | 0
case2 100MW购电上限 | 总成本l/($/year) | 投资成本/ ($/year) | 运维成本/ ($/year) | 燃料成本/ ($/year) | 购电成本/ ($/year) | 碳排放成本/ ($/year) |  | #VALUE! | #VALUE!
碳价100元=14$ | 157887796.8408 | 29600974.4591 | 8661026.8512 | 103956831.5206 | 507319.2557 | 15161598.7542 | 62.13% | 157.8878 | 15.1616
200 | 172747192.8675 | 33206092.315 | 8873552.0616 | 101399201.8667 | 397725.1985 | 28836998.7635 | 98.1009 | 172.7472 | 28.837
300 | 186988818.828 | 34799228.3774 | 8920264.4484 | 100572496.999 | 266434.3143 | 42315670.5327 |  | 186.9888 | 42.3157
400 | 200898125.0261 | 39556604.7175 | 9066889.6075 | 98086664.0286 | 205991.2292 | 53729906.1055 |  | 200.8981 | 53.7299
500 | 212656268.8311 | 65202018.7797 | 12894511.2439 | 84240785.5796 | 196051.5466 | 49507552.9474 |  | 212.6563 | 49.5076
600 | 222227939.4523 | 71404198.0764 | 13584146.8867 | 81111256.6851 | 229159.9971 | 54707501.2365 |  | 222.2279 | 54.7075
700 | 231193922.5057 | 73693322.7542 | 13837720.0696 | 80086823.186 | 204580.6551 | 61842460.1399 |  | 231.1939 | 61.8425
800 | 239832225.7227 | 77203321.0733 | 14391104.0378 | 78502428.7688 | 188022.1979 | 67306181.3334 |  | 239.8322 | 67.3062
900 | 248148878.48 | 81167175.7246 | 14834316.4672 | 76753403.7541 | 201934.9538 | 71989390.8593 |  | 248.1489 | 71.9894
1000 | 255988652.7403 | 83172996.4452 | 15034628.0238 | 75980052.5807 | 175379.1146 | 77757835.6533 |  | 255.9887 | 77.7578
[8 empty] | 0 | 0
case3 0MW购电上限 | 总成本l/($/year) | 投资成本/ ($/year) | 运维成本/ ($/year) | 燃料成本/ ($/year) | 购电成本/ ($/year) | 碳排放成本/ ($/year) |  | #VALUE! | #VALUE!
碳价100 | 172517414.6641 | 44667871.5627 | 16026218.1688 | 97859427.8171 | 0 | 13209186.4258 | 52.51% | 172.5174 | 13.2092
200 | 185374857.6025 | 50032069.6362 | 15658403.5716 | 94288173.1203 | 0 | 24597404.7923 | 90.5922 | 185.3749 | 24.5974
300 | 197357432.5206 | 53930926.1196 | 15292747.4619 | 92098572.5847 | 0 | 35221429.6268 |  | 197.3574 | 35.2214
400 | 208769762.6087 | 58826802.0558 | 15218079.328 | 89486306.6263 | 0 | 44297935.0388 |  | 208.7698 | 44.2979
500 | 219262013.8285 | 66825194.2043 | 15643846.2805 | 85333567.9774 | 0 | 50078680.1327 |  | 219.262 | 50.0787
600 | 228847403.1621 | 72513897.2323 | 16183383.1939 | 82482358.5217 | 0 | 55732876.6453 |  | 228.8474 | 55.7329
700 | 237933430.3423 | 76784889.711 | 16721528.5273 | 80446966.4647 | 0 | 61389181.2726 |  | 237.9334 | 61.3892
800 | 246631738.766 | 78656844.2676 | 16992734.3231 | 79617763.0239 | 0 | 68467798.0593 |  | 246.6317 | 68.4678
900 | 254987559.0178 | 81441374.0877 | 17347112.2672 | 78400178.42 | 0 | 74232426.9713 |  | 254.9876 | 74.2324
1000 | 263109611.172 | 83958961.4692 | 17428560.67 | 77403393.3619 | 0 | 79939134.8904 |  | 263.1096 | 79.9391
[8 empty] | 0 | 0
case4 | 总成本l/($/year) | 投资成本/ ($/year) | 运维成本/ ($/year) | 燃料成本/ ($/year) | 购电成本/ ($/year) | 碳排放成本/ ($/year) |  | #VALUE! | #VALUE!
碳价100 | 143666198.9661 | 33394565.1297 | 7021808.777 | 95272212.8998 | 0 | 7975179.3133 |  | 143.6662 | 7.9752
200 | 150587408.1568 | 37193577.6687 | 6962091.0535 | 92971207.9801 | 0 | 13457377.5748 |  | 150.5874 | 13.4574
300 | 157314869.8453 | 37207702.6782 | 6967268.4009 | 92953915.4898 | 0 | 20178912.8474 |  | 157.3149 | 20.1789
400 | 163859136.4589 | 43051840.8066 | 7138145.5607 | 89898213.0863 | 0 | 23719722.1973 |  | 163.8591 | 23.7197
500 | 167364280.8512 | 84511440.8135 | 13637396.3007 | 67652952.7792 | 0 | 1088479.3435 |  | 167.3643 | 1.0885
600 | 166542791.1219 | 101712623.5231 | 15645564.8166 | 59881702.9536 | 0 | -11672482.7057 |  | 166.5428 | -11.6725
700 | 163898740.2404 | 116019327.2818 | 17634908.7595 | 54577061.2369 | 0 | -25409551.1736 |  | 163.8987 | -25.4096
800 | 159632407.3073 | 128792200.7112 | 19726685.4215 | 50588506.7245 | 0 | -40622021.8762 |  | 159.6324 | -40.622
900 | 153443775.802 | 156667381.4737 | 28335895.3427 | 42752940.8674 | 0 | -75509864.7148 |  | 153.4438 | -75.5099
1000 | 144447354.713 | 168807058.2397 | 31320033.1862 | 39986597.3698 | 0 | -96954167.874 |  | 144.4474 | -96.9542
case1 | 总成本l/($/year) | 投资成本/ ($/year) | 运维成本/ ($/year) | 燃料成本/ ($/year) | 购电成本/ ($/year) | 碳排放成本/ ($/year)
1倍 | 505412215.675 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 45904401.9864 | 35795120.1637 |  |  | 505.4122
2倍 | 551316617.6614 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 91808803.9728 | 35795120.1637 |  |  | 551.3166
3倍 | 597221019.6478 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 137713205.9591 | 35795120.1637 |  |  | 597.221
4倍 | 643125421.6342 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 183617607.9455 | 35795120.1637 |  |  | 643.1254
5倍 | 689029823.6205 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 229522009.9319 | 35795120.1637 |  |  | 689.0298
6倍 | 734934225.6069 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 275426411.9183 | 35795120.1637 |  |  | 734.9342
7倍 | 780838627.5933 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 321330813.9046 | 35795120.1637 |  |  | 780.8386
8倍 | 826743029.5797 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 367235215.891 | 35795120.1637 |  |  | 826.743
9倍 | 872647431.566 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 413139617.8774 | 35795120.1637 |  |  | 872.6474
10倍 | 918551833.5524 | 13282566.3065 | 2248253.6667 | 408181873.5518 | 459044019.8638 | 35795120.1637 | 0.81743 |  | 918.5518
Case2 | 总成本l/($/year) | 投资成本/ ($/year) | 运维成本/ ($/year) | 燃料成本/ ($/year) | 购电成本/ ($/year) | 碳排放成本/ ($/year)
1倍 | 157887796.8408 | 29600974.4591 | 8661026.8512 | 103956831.5206 | 507319.2557 | 15161598.7542 | 1.504% |  | 157.8878
2倍 | 158377898.2474 | 29896353.598 | 8672936.95 | 103854727.0415 | 859575.4853 | 15070387.2225 |  |  | 158.3779
3倍 | 158753129.8375 | 30302410.8671 | 8686001.882 | 103706683.7907 | 1026334.8781 | 14961855.1971 |  |  | 158.7531
4倍 | 159062009.0775 | 30827802.8339 | 8702912.6206 | 103495066.688 | 1055184.6498 | 14847068.5582 |  |  | 159.062
5倍 | 159324610.6328 | 31237809.2884 | 8716398.0073 | 103318524.1407 | 1102508.9675 | 14768455.2848 |  |  | 159.3246
6倍 | 159540968.3676 | 31305415.6623 | 8718412.1441 | 103297937.2169 | 1261443.9144 | 14754781.9887 |  |  | 159.541 | [11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
7倍 | 159739783.1301 | 31509922.1062 | 8725151.6558 | 103211297.873 | 1340538.1866 | 14718769.6526 |  |  | 159.7398 | [11 empty] | 74.7227 | 149.4454 | 224.1681 | 298.8908 | 373.6135 | 448.3362 | 523.059 | 597.7817 | 672.5044 | 747.2271
8倍 | 159925820.1204 | 31632306.3324 | 8729442.5693 | 103163160.0886 | 1444327.3946 | 14697183.8718 |  |  | 159.9258 | [11 empty] | 0.92559 | 0.75895 | 0.77369 | 0.7644 | 0.70055 | 0.73147 | 0.67117 | 0.7423 | 0.80926 | 0.81817
9倍 | 160106080.3705 | 31854333.5617 | 8736338.5963 | 103061384.3949 | 1507707.6375 | 14661558.4545 |  |  | 160.1061 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10倍 | 160262027.5662 | 31973711.0184 | 8740574.5335 | 103010697.2892 | 1589362.2403 | 14642236.6759 | 能较好的应对电价波动 |  | 160.262 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
case3 |  | 160.262
不同电价，成本不变
case4
不同电价，成本不变

## 渗透率
| 碳排放 | 可再生能源利用率 | 装机占比 | 发电占比
Case1 | 8518.384 | - | - | -
Case2 | 5369.8644 | NaN | 0 | 0 | 36.96%
Case3 | 4989.9229 | 0.92764 | 0.35103 | 0.09907 |  | 7.075%
Case4 | 4857.999 | 0.96766 | 0.0056705 | 0.00073126 | 2.644%
a_result_Techindex
购电上限：
2MW | 5068.7551 | 0.93033 | 0.34449 | 0.07686
4MW | 5141.4497 | 0.93524 | 0.2799 | 0.056517
6MW | 5188.735 | 0.94335 | 0.23296 | 0.044094
8MW | 5227.332 | 0.95581 | 0.19158 | 0.034567
10MW | 5263.4332 | 0.95994 | 0.14706 | 0.024945
12MW | 5299.207 | 0.9536 | 0.1014 | 0.015595
14MW | 5299.207 | 0.9536 | 0.1014 | 0.015595
16MW | 5344.6263 | 0.90859 | 0.038147 | 0.0045865
18WM | 5369.6807 | 0.89664 | 0.001061 | 0.00012216
20MW | 5369.8644 | NaN | 0 | 0
30MW | 5369.9293 | NaN | 0 | 0
case1
不同碳价，碳排放量不变
case2 100MW购电上限 | 碳排放 | 可再生能源利用率 | 装机占比 | 发电占比
碳价100 | 5369.8644 | NaN | 0 | 0
200 | 5223.7016 | 0.875 | 0.03013 | 0.0035288 | 碳价拐点144元=20$
300 | 5163.7403 | 0.86768 | 0.091078 | 0.011325
400 | 5030.2151 | 0.93241 | 0.30122 | 0.050384
500 | 4324.0459 | 0.97245 | 0.64035 | 0.26563
600 | 4166.9515 | 0.96041 | 0.68162 | 0.31416
700 | 4110.8763 | 0.95496 | 0.69246 | 0.32895
800 | 4027.0611 | 0.94401 | 0.70884 | 0.353
900 | 3943.3438 | 0.92897 | 0.72716 | 0.37996
1000 | 3899.4162 | 0.91643 | 0.73586 | 0.39216
case3 0MW购电上限 | 碳排放 | 可再生能源利用率 | 装机占比 | 发电占比
碳价100 | 4989.9229 | 0.92764 | 0.35103 | 0.09907 | 14
200 | 4807.8221 | 0.93629 | 0.38497 | 0.11729 | 28
300 | 4696.1728 | 0.94962 | 0.42947 | 0.14507 | 42
400 | 4562.9714 | 0.94979 | 0.4942 | 0.18559 | 56
500 | 4351.2203 | 0.93788 | 0.57616 | 0.25003 | 70
600 | 4205.8351 | 0.93247 | 0.61823 | 0.29426 | 84
700 | 4102.049 | 0.92493 | 0.64369 | 0.32584 | 98
800 | 4059.7673 | 0.92131 | 0.65144 | 0.3367 | 112
900 | 3997.6818 | 0.91388 | 0.6658 | 0.35559 | 126
1000 | 3946.855 | 0.89518 | 0.68074 | 0.37106 | 140
case4 | 碳排放 | 可再生能源利用率 | 装机占比 | 发电占比
碳价100 | 4857.999 | 0.96766 | 0.0056705 | 0.00073126
200 | 4740.6691 | 0.98691 | 0.015322 | 0.0022593
300 | 4739.7873 | 0.97135 | 0.015887 | 0.0023259
400 | 4583.9749 | 0.98643 | 0.19933 | 0.036106
500 | 3449.673 | 0.98573 | 0.59596 | 0.27636
600 | 3053.4113 | 0.97679 | 0.67071 | 0.36625
700 | 2782.9238 | 0.97919 | 0.71225 | 0.43332
800 | 2579.5445 | 0.98163 | 0.74051 | 0.48733
900 | 2180.0034 | 0.98836 | 0.81131 | 0.59626
1000 | 2038.9455 | 0.9872 | 0.82607 | 0.63378
case1
不同电价，碳排放量不变
case2
1倍 | 5369.8644 | NaN | 0 | 0
2倍 | 5353.4 | 0.86562 | 0.020129 | 0.0023225
3倍 | 5333.5539 | 0.83458 | 0.046514 | 0.0054191
4倍 | 5312.1953 | 0.81853 | 0.078615 | 0.0093887
5倍 | 5297.3558 | 0.81631 | 0.1022 | 0.012506
6倍 | 5294.8425 | 0.80208 | 0.10598 | 0.01292
7倍 | 5294.8425 | 0.80208 | 0.10598 | 0.01292
8倍 | 5283.9336 | 0.78776 | 0.12379 | 0.015271
9倍 | 5277.0628 | 0.78996 | 0.13548 | 0.016959
10倍 | 5273.3666 | 0.78604 | 0.14164 | 0.017818
case3
不同电价，碳排放量不变
case4
不同电价，碳排放量不变